### Praesideo Multi Channel Interface PRS-16MCI

### Architects’ and Engineers’ Specifications

The multi-channel interface shall have a network interface for fiber optical hybrid cabling with dual network connections, capable of redundant loop operation. The fiber optic network interface of the multi-channel interface shall support multi-channel digital audio and control signals.

The multi-channel interface shall act as an interface to basic power amplifiers that do not have network connectivity, providing 14 configurable main output channels and 2 configurable spare output channels, to which network audio channels can be routed dynamically. It shall deliver the audio signals to the basic amplifiers with full control over these amplifiers.

The multi-channel interface shall have a supervision system to monitor the functions and operation of both itself and the connected amplifiers. It shall be capable of activating a spare amplifier channel to replace an amplifier channel that has reported a fault. It shall have loopthrough input and output, supporting failsafe mode to pass emergency calls through to the amplifiers, even if the unit itself fails. The unit shall support redundant group A/B switching and class-A loop wiring of the connected basic amplifiers, for which the multi-channel interface also shall incorporate a controller for multiple-line and loudspeaker supervision. Network connectivity status and fault conditions shall be displayed via LEDs on the front panel, including a status LED per connected amplifier channel. Fault conditions shall also be reported by the unit to a network connected system controller for logging purposes.

It shall be possible to power the multi-channel interface from the connected basic power amplifiers for easy installation or from the network. The unit shall be able to operate at a maximum operating temperature of 55°C to accommodate high density rack mounting.

The multi-channel interface shall have 32 control inputs for activation switches, with configurable supervision for open and short circuits. The control inputs shall have configurable functionality, such as automatically starting an emergency alarm in case of activation by a fire detector or control of background music volume.

The multi-channel interface shall have 16 control relay outputs, that can be configured via the network for various functions, such as fault indication or zone activity indication.

The multi-channel interface shall be certified by an independent test agency, such as the German TÜV, for compliancy to the standards EN 60849 and EN 54-16 for emergency sound systems.

The multi-channel interface cabinet shall be 19”-wide and 2U-high for easy rack mounting without the need for free rack space between units.

The multi-channel interface shall be a Praesideo PRS-16MCI, manufactured by Bosch Security Systems.