### Praesideo Loudspeaker Supervision Board LBB4441/00

### Architects’ and Engineers’ Specifications

The loudspeaker supervision board shall be a slave module that works in co-operation with a supervision control board, a master module, with the purpose of supervising the operation of a constant voltage loudspeaker and its loudspeaker line.

The loudspeaker supervision board shall be mountable in or on a loudspeaker (enclosure).

The loudspeaker supervision board shall be powered from the pilot tone of the amplifier, that drives the loudspeaker line with loudspeakers, without the need for an external power supply. It shall detect the pilot tone current through the voice coil of the loudspeaker as an indication of its operation.

The loudspeaker supervision board shall be polled by a supervision control board, mounted inside an amplifier, about the operational status of the loudspeaker and its wiring. The supervision control board shall be compatible with 70V and 100V constant voltage systems.

It shall communicate with the supervision control board via the existing loudspeaker line, requiring no additional wires, nor shielded wiring. The communication between the boards shall be on an inaudibly high frequency using advanced modulation techniques to minimize the risk for false positive fault detection. The monitoring of the connection and status of the loudspeaker and its loudspeaker line shall be continuous. Loudspeaker faults shall be detected and reported within 300 s, and line faults shall be detected and reported within 100 s.

The loudspeaker supervision board shall be able to operate at a maximum operating temperature of 55°C.

Fault conditions shall be transferred to the controller of the amplifier for report to a network connected system controller for logging purposes.

The loudspeaker supervision board shall be certified by an independent test agency, such as the German TÜV, for compliancy to the standards EN 60849 and EN 54-16 for emergency sound systems.

The loudspeaker supervision board shall be a Praesideo LBB4441/00, manufactured by Bosch Security Systems.