### Praesideo Line Supervision Set LBB4442/00

### Architects’ and Engineers’ Specifications

The line supervision set shall comprise a master module and a slave module, with the purpose of supervising the operation of constant voltage loudspeaker cabling.

The master module of the line supervision set shall be mountable inside a power amplifier and shall be under control of the amplifier controller. The slave module shall have screw terminals for connection to the (end of the) loudspeaker line, with loop through connections.

The master module shall be powered from the amplifier power supply, the slave module shall be powered from the pilot tone of the amplifier that is present on the loudspeaker line.

The slave module shall detect the presence of a pilot tone on the loudspeaker line as an indication that the loudspeaker line is not interrupted, nor shorted. It shall report this status to the master module. The line supervision set shall be compatible with 70V and 100V constant voltage systems.

The master module shall communicate with the slave module via the existing loudspeaker line, requiring no additional wires, nor shielded wiring. The communication between the master and the slave module shall be on an inaudibly high frequency using advanced modulation techniques to minimize the risk for false positive fault detection. The monitoring of the presence and status of the slave module shall be continuous. Loudspeaker line faults shall be detected and reported within 100 s.

It shall be possible to remotely configure the line supervision set via the network interface of the amplifier.

The master and slave modules shall be able to operate at a maximum operating temperature of 55°C.

Fault conditions shall be transferred to the controller of the amplifier for report to a network connected system controller for logging purposes.

The line supervision set shall be certified by an independent test agency, such as the German TÜV, for compliancy to the standards EN 60849 and EN 54-16 for emergency sound systems.

The line supervision set shall be a Praesideo LBB4442/00, manufactured by Bosch Security Systems.